## Modbus
Modbus RTU Request frame format
Start | SlaveAddress | FunctionCode | RegisterAddress | Length | CRC | End
3.5 x 8 bits of silence | 8 bits | 8 bits | 16 bits | 16 bits | 16 bits | 3.5 x 8 bits
Modbus RTU Reply frame format
Start | SlaveAddress | FunctionCode | BytesNumber | Data | CRC | End
3.5 x 8 bits of silence | Same as in request | Same as in request | 8 bits | n x 8bits | 16 bits | 3.5 x 8 bits
Exception
Start | SlaveAddress | FunctionCode | ErrorCode | CRC | End
3.5 x 8 bits of silence | Same as in request | request + 0x80 | 8 bits | 16 bits | 3.5 x 8 bits
FunctionCode
01 (0x01) | Read DO | Read Coil Status | Discrete | Read
02 (0x02) | Read DI | Read Input Status | Discrete | Read
03 (0x03) | Read AO | Read Holding Registers | 16 bit | Read
04 (0x04) | Read AI | Read Input Registers | 16 bit | Read
05 (0x05) | Write one DO | Force Single Coil | Discrete | Write
06 (0x06) | Write one AO | Preset Single Register | 16 bit | Write
15 (0x0F) | Multiple DO recording | Force Multiple Coils | Discrete | Write
16 (0x10) | Multiple AO recording | Preset Multiple Registers | 16 bit | Write
Standard Error Code | Text | Details
1 | Illegal Function | Function code received in the query is not recognized or allowed by server
2 | Illegal Data Address | Data address of some or all the required entities are not allowed or do not exist in server
3 | Illegal Data Value | Value is not accepted by server
4 | Server Device Failure | Unrecoverable error occurred while server was attempting to perform requested action
5 | Acknowledge | Server has accepted request and is processing it, but a long duration of time is required. This response is returned to prevent a timeout error from occurring in the client. client can next issue a Poll Program Complete message to determine whether processing is completed
6 | Server Device Busy | Server is engaged in processing a long-duration command; client should retry later
7 | Negative Acknowledge | Server cannot perform the programming functions; client should request diagnostic or error information from server
8 | Memory Parity Error | Server detected a parity error in memory; client can retry the request
10 | Gateway Path Unavailable | Specialized for Modbus gateways: indicates a misconfigured gateway
11 | Gateway Target Device Failed to Respond | Specialized for Modbus gateways: sent when server fails to respond
Customer Error Code
20 | Bad Slave Address | Used as internal error code for identify weather the message destination
21 | Not Supported Function | Legal modbus funtion and/or register addresses, but not yet implemented.
RegisterAddress | Name | Length (Words/Bytes/bits)
0x00 | V1 | 1W/2B/16b
0x01 | V2 | 1W/2B/16b
0x02 | V3 | 1W/2B/16b
0x03 | V4 | 1W/2B/16b
0x04 | I | 1W/2B/16b
0x05 | TEMP | 1W/2B/16b
0x06
0x07
BYTE | REQUEST | BYTE | REPLY
(Hex) | Field name | (Hex) | Field name
5 | Device address | 5 | Device address
4 | Functional code | 4 | Functional code
0 | Address of the first register Hi bytes | 2 | Number of bytes more
1 | Address of the first register Lo bytes | 0x00 | Register value Hi #30009
0 | Number of registers Hi bytes | 0xff | Register value Lo #30009
1 | Number of registers Lo bytes | crc_msb | Checksum CRC
crc_msb | Checksum CRC low | crc_lsb | Checksum CRC
crc_lsb | Checksum CRC high
Temperature Data Encoding
16bit signed integer

## GPIO
Morpho | Arduino Pin | Function | Note
PA0 | A0 | ADC_IN0 | MUX
PA1 | A1 | ADC_IN1 | TEMP Positive
PA2 | D1 | USART2_TX
PA3 | D0 | USART2_RX | DMA CH6
PA4 | A2 | ADC_IN4 | TEMP Negative
PA5 | D13 | LED_G
PA7 | D11 | USART1_TX_EN
PA9 | D8 | USART1_TX
PA10 | D2 | USART1_RX | DMA CH5
PB3 | D3 | MUX_A
PB5 | D4 | MUX_B
PB4 | D5 | MUX_C
PB8 | D15 | I2C SCL
PB9 | D14 | I2C SDA
PB10 | D6 | MOSFET_G0
PB6 | D10 | MOSFET_G1